{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":39,"n_cols":8,"rows_kept":39,"merged":[[1,0,1,7],[3,0,6,0],[3,1,6,1],[3,2,5,2],[3,3,6,3],[3,4,6,4],[7,0,24,0],[7,1,24,1],[7,2,9,2],[7,3,10,3],[7,4,10,4],[11,2,17,2],[11,3,17,3],[11,4,17,4],[18,2,24,2],[18,3,24,3],[18,4,24,4],[25,0,29,0],[25,1,29,1],[25,2,28,2],[25,3,29,3],[25,4,29,4],[30,0,33,0],[30,1,33,1],[30,2,32,2],[30,3,33,3],[30,4,33,4],[34,0,37,0],[34,1,37,1],[34,2,36,2],[34,3,37,3],[34,4,37,4],[38,1,38,7]],"flags":["formulas_cached_only"]}
["附件1"]
["广州市2018年国控企业污染源（废水重点）监督性监测结果（第二季度4月）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值"]
["黄埔区","广东粤华发电有限责任公司","5#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","2018-03-23","氮氧化物(mg/m3)",26,100]
[{"$nulls":5},"二氧化硫(mg/m3)",15,50]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03]
[null,null,"5#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1]
["黄埔区","中国石油化工股份有限公司广州分公司","3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值","2018-03-16","氮氧化物(mg/m3)",18,100]
[{"$nulls":5},"二氧化硫(mg/m3)",6,50]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03]
[null,null,"3#220t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1]
[null,null,"炼油区下风向边界点","《石油炼制工业污染物排放标准》（GB31570-2015）表5企业边界大气污染物排放限值","2018-03-19","总悬浮颗粒物(mg/m3)",{"v":0.1,"d":"0.100"},{"v":1,"d":"1.0"}]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(1.2×10-6 )",8e-06]
[{"$nulls":5},"非甲烷总烃(mg/m3)",{"v":1.6,"d":"1.60"},{"v":4,"d":"4.0"}]
[{"$nulls":5},"氯化氢(mg/m3)",0.027,0.2]
[{"$nulls":5},"甲苯(mg/m3)",0.095,0.8]
[{"$nulls":5},"苯(mg/m3)",0.025,0.4]
[{"$nulls":5},"二甲苯(mg/m3)",0.11,0.8]
[null,null,"化工区下风向边界点","《石油化学工业污染物排放标准》（GB31571-2015）表7企业边界大气污染物排放限值","2018-03-19","总悬浮颗粒物(mg/m3)",0.102,{"v":1,"d":"1.0"}]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(1.2×10-6 )",8e-06]
[{"$nulls":5},"非甲烷总烃(mg/m3)",1.24,{"v":4,"d":"4.0"}]
[{"$nulls":5},"氯化氢(mg/m3)",0.028,0.2]
[{"$nulls":5},"甲苯(mg/m3)",0.024,0.8]
[{"$nulls":5},"苯(mg/m3)",0.0066,0.4]
[{"$nulls":5},"二甲苯(mg/m3)",0.047,0.8]
["南沙区","广州珠江电力有限公司","1#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-03-15","二氧化硫(mg/m3)",25,50]
[{"$nulls":5},"氮氧化物(mg/m3)",43,100]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03]
[{"$nulls":5},"总VOCS(mg/m3)",0.76,"/"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1]
["南沙区","互太（番禺）纺织印染有限公司","1#、2#、3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-03-20","二氧化硫(mg/m3)",9,50]
[{"$nulls":5},"氮氧化物(mg/m3)",34,100]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03]
[null,null,"1#、2#、3#锅炉烟囱排放口",null,null,"林格曼黑度(级)",0.5,1]
["黄埔区","广州恒运东区热力有限公司","45#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-03-14","氮氧化物（mg/m3）",14,100]
[{"$nulls":5},"二氧化硫（mg/m3）",9,50]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03]
[null,null,"4#75t/h锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1]
["备注：","结果中“ND”表示未检出，括号中数值为该项目检出限。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}