{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":66,"n_cols":9,"rows_kept":66,"merged":[[1,0,1,8],[3,0,6,0],[3,1,6,1],[3,2,5,2],[3,3,6,3],[3,4,6,4],[7,0,10,0],[7,1,10,1],[7,2,9,2],[7,3,10,3],[7,4,10,4],[11,0,17,0],[11,1,17,1],[11,2,13,2],[11,3,17,3],[11,4,14,4],[15,2,17,2],[15,4,17,4],[18,0,21,0],[18,1,21,1],[18,2,20,2],[18,3,21,3],[18,4,21,4],[22,0,25,0],[22,1,25,1],[22,2,24,2],[22,3,25,3],[22,4,25,4],[26,0,29,0],[26,1,29,1],[26,2,28,2],[26,3,29,3],[26,4,29,4],[30,0,37,0],[30,1,37,1],[30,2,34,2],[30,3,37,3],[30,4,37,4],[38,0,55,0],[38,1,55,1],[38,2,43,2],[38,3,44,3],[38,4,44,4],[45,3,46,3],[45,4,52,4],[46,2,52,2],[47,3,55,3],[53,4,55,4],[56,0,59,0],[56,1,59,1],[56,2,58,2],[56,3,59,3],[56,4,59,4],[60,0,62,0],[60,1,62,1],[60,2,61,2],[60,3,62,3],[60,4,62,4],[63,2,63,8],[64,2,64,8],[65,1,65,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2018年国控企业污染源（废气重点）监督性监测结果（第二季度6月）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标"]
["荔湾区","广州发电厂有限公司","1#、2#、3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-04-26","二氧化硫（mg/m3）",9,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",31,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#、3#220t/h锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","广东粤华发电有限责任公司","6#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","2018-05-23","氮氧化物(mg/m3)",34,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",30,50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"5#、6#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","中国石油化工股份有限公司广州分公司","3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值","2018-04-23","氮氧化物(mg/m3)",22,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",8,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"3#220t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"1#、2#CFB炉排放口",null,"2018-04-25","氮氧化物(mg/m3)",20,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",7,50,"是"]
[{"$nulls":5},"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州珠江电力有限公司","2#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-05-04","二氧化硫(mg/m3)",22,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",39,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,"广州华润热电有限公司","2#30万千瓦发电机组处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-05-07","二氧化硫(mg/m3)",16,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3）",36,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"2#30万千瓦发电机组烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["增城区","广州市旺隆热电有限公司","2#420t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-05-03","二氧化硫(mg/m3)",8,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",22,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.03,"是"]
[null,null,"1#、2#420t/h锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["花都区","广州市珠江水泥有限公司","窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值\n","2018-05-25","氮氧化物(mg/m3)",242,400,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",51,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.05,"是"]
[{"$nulls":5},"氟化物(mg/m3)","ND(0.06)",3,"是"]
[{"$nulls":5},"氨(mg/m3)","ND(0.25)",10,"是"]
[null,null,"窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","/"]
[null,null,"下风向厂界外10米范围内",null,null,"氨(mg/m3)","ND(0.25)",{"v":1,"d":"1.0"},"是"]
[null,null,"下风向厂界外20米处",null,null,"总悬浮颗粒物(mg/m3)","0.158（扣参考值）",0.5,"是"]
["花都区","广州市越堡水泥有限公司","回转窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值+《水泥窑协同处置固体废物污染控制标准》表1协同处置固体废物水泥窑大气污染物最高允许排放浓度","2018-04-19","氮氧化物（mg/m3）",278,400,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",25,100,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(0.0025)",0.05,"是"]
[{"$nulls":5},"氟化氢（mg/m3）",0.63,1,"是"]
[{"$nulls":5},"氟化物（mg/m3）","ND(0.06)",3,"是"]
[{"$nulls":5},"氨（mg/m3）","ND(0.25)",10,"是"]
[null,null,"回转窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","/"]
[null,null,"下风向厂界外20米处","《水泥工业大气污染物排放标准》(GB 4519-2013)表3 大气污染物无组织排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表3作业场所颗粒物无组织排放限值","2018-04-19","总悬浮颗粒物（mg/m3）","0.029（扣参考值）",0.5,"是"]
[null,null,"下风向厂界外10米范围内",null,null,"氨（mg/m3）",0.158,{"v":1,"d":"1.0"},"是"]
[{"$nulls":3},"《恶臭污染物排放标准》（GB14554-93）表1 恶臭污染物厂界标准值",null,"氨（mg/m3）",0.116,1.5,"是"]
[{"$nulls":5},"硫化氢（mg/m3）","ND(0.0003)",0.06,"是"]
[{"$nulls":5},"甲硫醚（mg/m3）","ND(0.0004)",0.07,"是"]
[{"$nulls":5},"甲硫醇（mg/m3）","ND(0.0006)",0.007,"是"]
[{"$nulls":5},"苯乙烯（mg/m3）","ND(0.0005)",{"v":5,"d":"5.0"},"是"]
[{"$nulls":5},"二甲二硫（mg/m3）","ND(0.0004)",0.06,"是"]
[null,null,"厂界点1#",null,"2018-04-26","臭气浓度（无量纲）",12,20,"是"]
[null,null,"厂界点2#",null,null,"臭气浓度（无量纲）",13,20,"是"]
[null,null,"厂界点3#",null,null,"臭气浓度（无量纲）",14,20,"是"]
["黄埔区","广州恒运东区热力有限公司","5#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-04-26","氮氧化物（mg/m3）",18,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",6,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"5#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州珠江天然气发电有限公司","2#发电机组","《火电厂大气污染物排放标准》（GB13223-2011）表1火力发电锅炉及燃气轮组大气污染物排放浓度限值（天然气锅炉及燃气轮组）","2018-06-11","氮氧化物(mg/m3)",20,50,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND(3)",35,"是"]
[null,null,"2#发电机组烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州市梅山热电厂有限公司","停产"]
["黄埔区","广州瑞明电力股份有限公司","停产"]
["备注：","结果中“ND”表示未检出，括号中数值为该项目检出限。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}