{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":12,"n_cols":9,"rows_kept":12,"merged":[[1,0,1,8],[3,0,10,0],[3,1,10,1],[3,2,5,2],[3,3,6,3],[3,4,6,4],[7,2,9,2],[7,3,10,3],[7,4,10,4],[11,1,11,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2018年国控企业污染源（废气重点）监督性监测结果（第三季度8月）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标"]
["黄埔区","广州恒运东区热力有限公司","5#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-08-06","氮氧化物（mg/m3）",25,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",8,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"5#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"4#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-08-07","氮氧化物（mg/m3）",23,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",8,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"4#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["备注：","结果中“ND”表示未检出，括号中数值为该项目检出限。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}