{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":61,"n_cols":9,"rows_kept":61,"merged":[[0,0,0,8],[1,0,1,8],[3,0,5,0],[3,1,5,1],[3,2,4,2],[3,3,5,3],[3,4,5,4],[6,0,14,0],[6,1,14,1],[6,3,14,3],[6,4,7,4],[8,4,9,4],[10,4,11,4],[12,2,13,2],[12,4,14,4],[15,0,21,0],[15,1,21,1],[15,2,17,2],[15,3,21,3],[15,4,17,4],[18,2,20,2],[18,4,21,4],[22,0,26,0],[22,1,26,1],[22,2,25,2],[22,3,26,3],[22,4,26,4],[27,0,40,0],[27,1,40,1],[27,2,29,2],[27,3,30,3],[27,4,30,4],[31,2,33,2],[31,3,33,3],[31,4,33,4],[34,2,36,2],[34,3,36,3],[34,4,36,4],[37,2,39,2],[37,3,40,3],[37,4,40,4],[41,0,47,0],[41,1,47,1],[41,2,43,2],[41,3,47,3],[41,4,43,4],[44,2,46,2],[44,4,47,4],[48,0,58,0],[48,1,58,1],[48,2,53,2],[48,3,58,3],[48,4,58,4],[55,2,56,2],[57,2,58,2],[60,1,60,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2018年国控企业污染源（废气重点）监督性监测结果（第4季度）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标"]
["南沙区","广州珠江天然气发电有限公司","2#发电机组","《火电厂大气污染物排放标准》（GB13223-2011）表1火力发电锅炉及燃气轮组大气污染物排放浓度限值（天然气锅炉及燃气轮组）","2018-10-22","氮氧化物(mg/m3)",19,50,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND(3)",35,"是"]
[null,null,"2#发电机组烟囱排放口",null,null,"林格曼黑度（级）",0,1,"是"]
["黄埔区","鞍钢联众（广州）不锈钢有限公司","CAPL退火炉冷却段d","《轧钢工业大气污染物排放标准》（GB28665-2012）表2+广东省《大气污染物排放限值》（DB4427-2001）第二时段二级标准","2018-10-23","颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"CAPL退火炉冷却段e",null,null,"颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"WRAP退火炉冷却段a",null,"2018-10-24","颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"WRAP退火炉冷却段c",null,null,"颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"HAPL珠击段a",null,"2018-10-26","颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"HAPL珠击段b",null,null,"颗粒物（粉尘）（mg/m3）","＜20",20,"是"]
[null,null,"HAPL-ARP",null,"2018-10-25","氮氧化物（mg/m3）",33,120,"是"]
[{"$nulls":5},"氟化物（mg/m3）",0.18,9,"是"]
[null,null,"HAPL硫酸酸洗区",null,null,"硫酸雾（mg/m3）",1.02,10,"是"]
["增城区","广州中电荔新电力实业有限公司","1#（33万千瓦）锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-10-23","氮氧化物（mg/m3）",20,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",13,50,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(2.5×10-3)",0.03,"是"]
[null,null,"2#（33万千瓦）锅炉处理后",null,"2018-10-24","氮氧化物（mg/m3）",36,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",14,50,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(2.5×10-3)",0.03,"是"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州越威纸业有限公司","130t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-10-30","*颗粒物（烟尘）(mg/m3)","＜20",20,"/"]
[{"$nulls":5},"氮氧化物（mg/m3）",37,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",8,50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"130t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州珠江电力有限公司","1#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-10-31","二氧化硫(mg/m3)",20,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",50,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"2#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉","二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/"]
[null,null,"3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉","二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/"]
[null,null,"4#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-11-01","二氧化硫(mg/m3)",27,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",45,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"3#、4#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","广东粤华发电有限责任公司","5#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","停炉","氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
[null,null,"6#锅炉处理后",null,"2018-11-07","氮氧化物(mg/m3)",24,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",14,50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"5#、6#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["花都区","广州市珠江水泥有限公司","窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值\n","2018-10-30","*颗粒物（烟尘）(mg/m3)","＜20",30,"/"]
[{"$nulls":5},"氮氧化物(mg/m3)",195,400,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",13,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)",0.0035,0.05,"是"]
[{"$nulls":5},"氟化物(mg/m3)","ND(0.06)",3,"是"]
[{"$nulls":5},"氨(mg/m3)",6.94,10,"是"]
[null,null,"窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","/"]
[null,null,"下风向边界点1#",null,null,"氨(mg/m3)",0.142,{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"总悬浮颗粒物(mg/m3)","0.003（扣参考值）",0.5,"是"]
[null,null,"下风向边界点2#",null,null,"氨(mg/m3)",0.118,{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"总悬浮颗粒物(mg/m3)","0.020（扣参考值）",0.5,"是"]
["备注：","①结果中“ND”表示未检出，括号中数值为该项目检出限。"]
[null,"②表中*颗粒物（烟尘）均为实测浓度，按照GB/T 16157-1996修改单，采用本标准测定颗粒物浓度小于等于20 mg/m3时，测定结果表述为＜20 mg/m3,无法换算为基准含氧量状态下的基准排放浓度，故不做达标评价。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}