{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":2,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":148,"n_cols":9,"rows_kept":148,"merged":[[1,0,1,8],[3,0,10,0],[3,1,10,1],[3,2,5,2],[3,3,6,3],[3,4,6,4],[7,2,9,2],[7,3,10,3],[7,4,10,4],[11,0,18,0],[11,1,18,1],[11,2,13,2],[11,3,14,3],[11,4,14,4],[15,2,17,2],[15,3,18,3],[15,4,18,4],[19,0,30,0],[19,1,30,1],[19,2,21,2],[19,3,22,3],[19,4,22,4],[23,2,26,2],[23,3,26,3],[23,4,26,4],[27,2,30,2],[27,3,30,3],[27,4,30,4],[31,0,45,0],[31,1,45,1],[31,2,33,2],[31,3,34,3],[31,4,34,4],[35,2,37,2],[35,3,38,3],[35,4,38,4],[39,2,41,2],[39,3,41,3],[39,4,41,4],[42,2,44,2],[42,3,45,3],[42,4,45,4],[46,0,55,0],[46,1,55,1],[46,2,49,2],[46,3,50,3],[46,4,50,4],[51,2,54,2],[51,3,55,3],[51,4,55,4],[56,0,63,0],[56,1,63,1],[56,2,58,2],[56,3,63,3],[56,4,59,4],[60,2,62,2],[60,4,63,4],[64,0,70,0],[64,1,70,1],[64,2,66,2],[64,3,70,3],[64,4,66,4],[67,2,69,2],[67,4,70,4],[71,0,74,0],[71,1,74,1],[71,2,73,2],[71,3,74,3],[71,4,74,4],[75,0,89,0],[75,1,89,1],[75,3,89,3],[75,4,76,4],[77,4,80,4],[81,2,82,2],[81,4,84,4],[83,2,84,2],[85,2,86,2],[85,4,86,4],[87,2,88,2],[87,4,89,4],[90,0,96,0],[90,1,96,1],[90,2,92,2],[90,3,92,3],[90,4,92,4],[93,2,95,2],[93,3,96,3],[93,4,96,4],[97,0,103,0],[97,1,103,1],[97,2,99,2],[97,3,103,3],[97,4,99,4],[100,2,102,2],[100,4,103,4],[104,0,113,0],[104,1,113,1],[104,2,110,2],[104,3,113,3],[104,4,113,4],[114,0,127,0],[114,1,127,1],[114,2,119,2],[114,3,120,3],[114,4,120,4],[121,3,122,3],[121,4,126,4],[122,2,126,2],[123,3,127,3],[128,0,131,0],[128,1,131,1],[128,2,130,2],[128,3,131,3],[128,4,131,4],[132,0,136,0],[132,1,136,1],[132,2,135,2],[132,3,136,3],[132,4,136,4],[137,0,144,0],[137,1,144,1],[137,2,140,2],[137,3,140,3],[137,4,140,4],[141,2,144,2],[141,3,144,3],[141,4,144,4],[145,2,145,8],[146,2,146,8],[147,1,147,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2018年国控企业污染源（废气重点）监督性监测结果（第一季度2月）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标"]
["荔湾区","广州发电厂有限公司","1#、2#、3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-12","二氧化硫（mg/m3）",7,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",24,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#、3#220t/h锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"4#、5#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","监测期间停炉","二氧化硫（mg/m3）","/",50,"/"]
[{"$nulls":5},"氮氧化物（mg/m3）","/",100,"/"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
[null,null,"4#、5#220t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
["黄埔区","广东粤华发电有限责任公司","6#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","2018-01-11","氮氧化物(mg/m3)",36,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",23,50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"5#、6#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"5#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","监测期间停炉","氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
[null,null,"5#锅炉烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
["黄埔区","中国石油化工股份有限公司广州分公司","3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值+表1规定的限值","监测期间停炉","氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"汞及其化合物(mg/m3)","/",0.03,"/"]
[null,null,"3#220t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
[null,null,"4#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值+表1规定的限值","2018-01-26","氮氧化物(mg/m3)",22,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",10,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[{"$nulls":5},"林格曼黑度（级）",0.5,1,"是"]
[null,null,"1#、2#CFB炉排放口","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值","2018-01-23","氮氧化物(mg/m3)",22,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",7,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[{"$nulls":5},"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州珠江电力有限公司","2#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-17","二氧化硫(mg/m3)",30,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",39,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-18","二氧化硫(mg/m3)",24,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",37,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"3#、4#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"4#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-19","二氧化硫(mg/m3)",30,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",41,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","监测期间停炉","二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/"]
[null,null,"1#、2#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
["南沙区","互太（番禺）纺织印染有限公司","1#、2#、3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","监测期间停炉","颗粒物（烟尘）(mg/m3)","/",20,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/"]
[null,null,"1#、2#、3#锅炉烟囱排放口",null,null,"林格曼黑度(级)","/",1,"/"]
[null,null,"4#、5#、6#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-16","颗粒物（烟尘）(mg/m3)",13,20,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",6,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",68,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"4#、5#、6#锅炉处理后烟囱排放口",null,null,"林格曼黑度(级)",0.5,1,"是"]
["南沙区","广州华润热电有限公司","1#30万千瓦发电机组处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-23","二氧化硫(mg/m3)",11,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3）",49,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#30万千瓦发电机组烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"2#30万千瓦发电机组处理后",null,"2018-01-24","二氧化硫(mg/m3)",15,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3）",44,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"2#30万千瓦发电机组烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","广州恒运热电（D）厂有限责任公司","8#（30万千瓦）锅炉\n处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-12","二氧化硫（mg/m3）",15,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",31,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"9#（30万千瓦）锅炉\n处理后",null,"2018-01-11","二氧化硫（mg/m3）",22,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",43,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"8#、9#（30千瓦）锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","广州恒运企业集团股份有限公司","6#、7#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-22","二氧化硫（mg/m3）",13,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",35,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"6#、7#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["黄埔区","鞍钢联众（广州）不锈钢有限公司","CAPL退火炉冷却段b","《轧钢工业大气污染物排放标准》（GB28665-2012）表2+广东省《大气污染物排放限值》（DB4427-2001）第二时段二级标准","2018-01-08","颗粒物（mg/m3）",13,20,"是"]
[null,null,"CAPL退火炉冷却段c",null,null,"颗粒物（mg/m3）",12,20,"是"]
[null,null,"WRAP退火冷却段a",null,"2018-01-09","颗粒物（mg/m3）",13,20,"是"]
[null,null,"WRAP退火冷却段b",null,null,"颗粒物（mg/m3）",12,20,"是"]
[null,null,"WRAP退火冷却段c",null,null,"颗粒物（mg/m3）",13,20,"是"]
[null,null,"WRAP退火冷却段d",null,null,"颗粒物（mg/m3）",13,20,"是"]
[null,null,"WRAP退火加热段a",null,"2018-01-10","氮氧化物（mg/m3）",180,300,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）","ND(3)",150,"是"]
[null,null,"WRAP退火加热段b",null,null,"氮氧化物（mg/m3）",159,300,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）","ND(3)",150,"是"]
[null,null,"HAPL-ARP",null,"2018-01-15","氮氧化物（mg/m3）",9,120,"是"]
[{"$nulls":5},"氟化物（mg/m3）","ND(0.06)",{"v":9,"d":"9.0"},"是"]
[null,null,"CAPL混酸酸洗区",null,"2018-01-11","氮氧化物（mg/m3）",42,300,"是"]
[{"$nulls":5},"氟化物（mg/m3）","ND(0.06)",{"v":6,"d":"6.0"},"是"]
[null,null,"CAPL中性电解区",null,null,"硫酸雾（mg/m3）",{"v":0.6,"d":"0.60"},10,"是"]
["增城区","广州市旺隆热电有限公司","1#420t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-16","二氧化硫(mg/m3)",6,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",30,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.03,"是"]
[null,null,"2#420t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-17","二氧化硫(mg/m3)",6,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",23,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.03,"是"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["增城区","广州中电荔新电力实业有限公司","1#（33万千瓦）锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-18","氮氧化物（mg/m3）",39,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",14,50,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(2.5×10-3)",0.03,"是"]
[null,null,"2#（33万千瓦）锅炉处理后",null,"2018-01-19","氮氧化物（mg/m3）",37,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",21,50,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(2.5×10-3)",0.03,"是"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["花都区","广州市珠江水泥有限公司","窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值\n","2018-01-16","颗粒物（烟尘）(mg/m3)",15,30,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",166,400,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",6,100,"是"]
[{"$nulls":5},"一氧化碳(mg/m3)",140,"/","/"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.05,"是"]
[{"$nulls":5},"氟化物(mg/m3)","ND(0.06)",3,"是"]
[{"$nulls":5},"氨(mg/m3)","ND(0.25)",10,"是"]
[null,null,"窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","/"]
[null,null,"下风向厂界外10米范围内",null,null,"氨(mg/m3)","0.026",{"v":1,"d":"1.0"},"是"]
[null,null,"下风向厂界外20米处",null,null,"总悬浮颗粒物(mg/m3)","0.003（扣背景值）",0.5,"是"]
["花都区","广州市越堡水泥有限公司","回转窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值\n","2018-01-17","烟尘（mg/m3）",17,30,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",302,400,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",36,100,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(0.0025)",0.05,"是"]
[{"$nulls":5},"氟化物（mg/m3）","ND(0.06)",3,"是"]
[{"$nulls":5},"氨（mg/m3）",1.57,10,"是"]
[null,null,"回转窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","/"]
[null,null,"下风向厂界外20米处","《水泥工业大气污染物排放标准》(GB 4519-2013)表3 大气污染物无组织排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表3作业场所颗粒物无组织排放限值","2018-01-17","总悬浮颗粒物（mg/m3）","0.002（扣参考值）",0.5,"是"]
[null,null,"下风向厂界外10米范围内",null,null,"氨（mg/m3）","ND(0.025)",{"v":1,"d":"1.0"},"是"]
[{"$nulls":3},"《恶臭污染物排放标准》（GB14554-93）表1 恶臭污染物厂界标准值",null,"硫化氢（mg/m3）","ND(0.0003)",0.06,"是"]
[{"$nulls":5},"甲硫醚（mg/m3）","ND(0.0004)",0.07,"是"]
[{"$nulls":5},"甲硫醇（mg/m3）","ND(0.0006)",0.007,"是"]
[{"$nulls":5},"二甲二硫（mg/m3）","ND(0.0004)",0.06,"是"]
[null,null,"厂界点",null,"2018-02-05","臭气浓度（无量纲）",13,20,"是"]
["黄埔区","广州恒运东区热力有限公司","5#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2018-01-19","氮氧化物（mg/m3）",20,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",7,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"5#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区","广州越威纸业有限公司","130t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","1-2月停炉","颗粒物（烟尘）(mg/m3)","/",20,"/"]
[{"$nulls":5},"氮氧化物（mg/m3）","/",100,"/"]
[{"$nulls":5},"二氧化硫（mg/m3）","/",50,"/"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
[null,null,"130t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
["南沙区","广州珠江天然气发电有限公司","1#发电机组","《火电厂大气污染物排放标准》（GB13223-2011）表1火力发电锅炉及燃气轮组大气污染物排放浓度限值（天然气锅炉及燃气轮组）","2018-01-15","烟尘(mg/m3)","ND(5)",5,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",34,50,"是"]
[{"$nulls":5},"林格曼黑度（级）",0.5,1,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND(3)",35,"是"]
[null,null,"2#发电机组","《火电厂大气污染物排放标准》（GB13223-2011）表1火力发电锅炉及燃气轮组大气污染物排放浓度限值（天然气锅炉及燃气轮组）","2018-01-15","烟尘(mg/m3)","ND(5)",5,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",28,50,"是"]
[{"$nulls":5},"林格曼黑度（级）",0.5,1,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND(3)",35,"是"]
["南沙区","广州市梅山热电厂有限公司","停产"]
["黄埔区","广州瑞明电力股份有限公司","停产"]
["备注：","结果中“ND”表示未检出，括号中数值为该项目检出限。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}