{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":89,"n_cols":9,"rows_kept":89,"merged":[[1,0,1,8],[3,0,9,0],[3,1,9,1],[3,2,5,2],[3,3,9,3],[3,4,9,4],[7,2,9,2],[10,0,53,0],[10,1,53,1],[10,2,12,2],[10,3,21,3],[10,4,13,4],[14,2,17,2],[14,4,17,4],[18,2,20,2],[18,4,21,4],[22,2,28,2],[22,3,37,3],[22,4,53,4],[30,2,37,2],[38,2,45,2],[38,3,53,3],[46,2,53,2],[54,0,63,0],[54,1,63,1],[54,2,57,2],[54,3,63,3],[54,4,58,4],[59,2,62,2],[59,4,63,4],[64,0,67,0],[64,1,71,1],[64,2,66,2],[64,3,67,3],[64,4,67,4],[68,0,71,0],[68,2,70,2],[68,3,71,3],[68,4,71,4],[72,0,75,0],[72,1,75,1],[72,2,74,2],[72,3,75,3],[72,4,75,4],[76,0,82,0],[76,1,82,1],[76,2,78,2],[76,3,78,3],[76,4,78,4],[79,2,81,2],[79,3,82,3],[79,4,81,4],[83,0,85,0],[83,1,85,1],[83,3,85,3],[83,4,85,4],[84,2,85,2],[86,2,86,8],[87,2,87,8],[88,1,88,8],[89,1,89,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2019年国控企业污染源（废气重点）监督性监测结果（第1季度）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标"]
["黄埔区","广东粤华发电有限责任公司","5#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2规定的限值","2019-01-21","氮氧化物(mg/m3)",30,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",12,50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
[null,null,"5#、6#锅炉处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"6#锅炉处理后",null,null,"氮氧化物(mg/m3)",40,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND(3)",50,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","/",0.03,"/"]
["黄埔区","中国石油化工股份有限公司广州分公司","3#220t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值","2019-01-07","氮氧化物(mg/m3)",16,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",6,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)",0.003,0.03,"是"]
[null,null,"3#220t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"4#220t/h锅炉处理后",null,"停开","氮氧化物(mg/m3)","/",100,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"汞及其化合物(mg/m3)","/",0.03,"/"]
[{"$nulls":5},"林格曼黑度（级）","/",1,"/"]
[null,null,"1#、2#CFB炉排放口",null,"2019-01-08","氮氧化物(mg/m3)",19,100,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",13,50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#CFB炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
[null,null,"炼油区下风向边界点1#","《石油炼制工业污染物排放标准》（GB31570-2015）表5企业边界大气污染物排放限值","2019-01-04","总悬浮颗粒物(mg/m3)",0.118,{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(5×10-8)",8e-06,"是"]
[{"$nulls":5},"非甲烷总烃(mg/m3)","ND(0.07)",{"v":4,"d":"4.0"},"是"]
[{"$nulls":5},"氯化氢(mg/m3)",0.12,0.2,"是"]
[{"$nulls":5},"甲苯(mg/m3)",0.007,0.8,"是"]
[{"$nulls":5},"苯(mg/m3)",0.011,0.4,"是"]
[{"$nulls":5},"二甲苯(mg/m3)",0.011,0.8,"是"]
[{"$nulls":5},"臭气浓度","<10","/","/"]
[null,null,"炼油区下风向边界点2#",null,null,"总悬浮颗粒物(mg/m3)",0.156,1,"是"]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(5×10-8)",8e-06,"是"]
[{"$nulls":5},"非甲烷总烃(mg/m3)",0.12,4,"是"]
[{"$nulls":5},"氯化氢(mg/m3)",0.17,0.2,"是"]
[{"$nulls":5},"甲苯(mg/m3)",0.009,0.8,"是"]
[{"$nulls":5},"苯(mg/m3)",{"v":0.01,"d":"0.010"},0.4,"是"]
[{"$nulls":5},"二甲苯(mg/m3)",0.013,0.8,"是"]
[{"$nulls":5},"臭气浓度","<10","/","/"]
[null,null,"化工区下风向边界点1#","《石油炼制工业污染物排放标准》（GB31570-2015）表5企业边界大气污染物排放限值",null,"总悬浮颗粒物(mg/m3)",0.099,1,"是"]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(5×10-8)",8e-06,"是"]
[{"$nulls":5},"非甲烷总烃(mg/m3)",0.12,4,"是"]
[{"$nulls":5},"氯化氢(mg/m3)",0.15,0.2,"是"]
[{"$nulls":5},"甲苯(mg/m3)",{"v":0.01,"d":"0.010"},0.8,"是"]
[{"$nulls":5},"苯(mg/m3)",0.012,0.4,"是"]
[{"$nulls":5},"二甲苯(mg/m3)",0.018,0.8,"是"]
[{"$nulls":5},"臭气浓度","<10","/","/"]
[null,null,"化工区下风向边界点2#",null,null,"总悬浮颗粒物(mg/m3)",0.097,{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"苯并[a]芘(mg/m3)","ND(5×10-8)",8e-06,"是"]
[{"$nulls":5},"非甲烷总烃(mg/m3)",0.22,{"v":4,"d":"4.0"},"是"]
[{"$nulls":5},"氯化氢(mg/m3)",0.18,0.2,"是"]
[{"$nulls":5},"甲苯(mg/m3)",0.008,0.8,"是"]
[{"$nulls":5},"苯(mg/m3)",0.009,0.4,"是"]
[{"$nulls":5},"二甲苯(mg/m3)",0.012,0.8,"是"]
[{"$nulls":5},"臭气浓度","<10","/","/"]
["南沙区","互太（番禺）纺织印染有限公司","1#、2#、3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-07","颗粒物（烟尘)(mg/m3)","<20",20,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)",8,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",21,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#、2#、3#锅炉烟囱排放口",null,null,"林格曼黑度(级)",0.5,1,"是"]
[null,null,"4#、5#、6#锅炉处理后",null,"2019-01-08","颗粒物（烟尘)(mg/m3)","<20",20,"/"]
[{"$nulls":5},"二氧化硫(mg/m3)",6,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3)",14,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"4#、5#、6#锅炉烟囱排放口",null,null,"林格曼黑度(级)",1,1,"是"]
["南沙区","广州华润热电有限公司","1#30万千瓦发电机组处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-09","二氧化硫(mg/m3)",13,50,"是"]
[{"$nulls":5},"氮氧化物(mg/m3）",37,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是"]
[null,null,"1#30万千瓦发电机组处理后烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["南沙区",null,"2#30万千瓦发电机组处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉检修","二氧化硫(mg/m3)","/",50,"/"]
[{"$nulls":5},"氮氧化物(mg/m3）","/",100,"/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/"]
[null,null,"2#30万千瓦发电机组处理后烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/"]
["黄埔区","广州恒运企业集团股份有限公司","6#、7#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-09","二氧化硫（mg/m3）",15,50,"是"]
[{"$nulls":5},"氮氧化物（mg/m3）",44,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"6#、7#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是"]
["增城区","广州中电荔新电力实业有限公司","1#（33万千瓦）锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-03","氮氧化物（mg/m3）",36,100,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",21,50,"是"]
[{"$nulls":5},"汞（mg/m3）","ND(0.0025)",0.03,"是"]
[null,null,"2#（33万千瓦）锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉","氮氧化物（mg/m3）","/",100,"/"]
[{"$nulls":5},"二氧化硫（mg/m3）","/",50,"/"]
[{"$nulls":5},"汞（mg/m3）","/",0.03,"/"]
[null,null,"1#、2#锅炉烟囱排放口",null,"2019-01-03","林格曼黑度（级）",0.5,1,"是"]
["黄埔区","广东南方碱业股份有限公司","石灰工序废气排气筒","《大气污染物排放限值》（DB44/27-2001）第二时段二级标准","2019-01-23","颗粒物（粉尘)(mg/m3)",12,120,"是"]
[null,null,"重灰工序重灰尾气排气筒",null,null,"颗粒物（粉尘)(mg/m3)",25,120,"是"]
[{"$nulls":5},"氨(mg/m3)",36.3,"/","/"]
["南沙区","广州市梅山热电厂有限公司","停产"]
["黄埔区","广州瑞明电力股份有限公司","停产"]
["备注：","结果中“ND”表示未检出，括号中数值为该项目检出限。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}