{"text_format":"3","workbook":"xls","n_sheets":3,"sheets":["废气","Sheet2","Sheet3"],"not_rendered":{"external_links":1,"defined_names":3},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"废气","index":0,"n_rows":86,"n_cols":10,"rows_kept":86,"merged":[[1,0,1,8],[3,0,17,0],[3,1,17,1],[3,2,5,2],[3,3,5,3],[3,4,5,4],[6,2,8,2],[6,3,9,3],[6,4,9,4],[10,2,12,2],[10,3,13,3],[10,4,13,4],[10,9,11,9],[14,2,16,2],[14,3,17,3],[14,4,17,4],[14,9,15,9],[18,0,24,0],[18,1,24,1],[18,2,20,2],[18,3,24,3],[18,4,20,4],[18,9,19,9],[21,2,23,2],[21,4,23,4],[21,9,22,9],[25,0,31,0],[25,1,31,1],[25,3,31,3],[25,4,28,4],[25,9,29,9],[29,2,30,2],[29,4,30,4],[30,9,31,9],[32,0,41,0],[32,1,41,1],[32,2,37,2],[32,3,41,3],[32,4,41,4],[32,9,41,9],[42,0,66,0],[42,1,66,1],[42,2,48,2],[42,3,49,3],[42,4,44,4],[42,9,44,9],[45,4,48,4],[45,9,48,9],[50,3,66,3],[50,4,64,4],[50,9,66,9],[51,2,57,2],[58,2,64,2],[65,4,66,4],[67,0,74,0],[67,1,74,1],[67,2,69,2],[67,3,70,3],[67,4,70,4],[67,9,68,9],[71,2,73,2],[71,3,74,3],[71,4,74,4],[71,9,72,9],[75,0,80,0],[75,1,80,1],[75,2,76,2],[75,3,80,3],[75,4,80,4],[75,9,80,9],[79,2,80,2],[81,2,81,8],[82,2,82,8],[83,2,83,8],[84,1,84,8],[85,1,85,8]],"flags":["formulas_cached_only"]}
["附件2"]
["广州市2019年国控企业污染源（废气重点）监督性监测结果（3月报送）"]
["行政区","企业名称","监测点名称","执行标准名称","监测日期","监测项目名称（单位）","污染物浓度","标准限值","是否达标","数据提供单位"]
["南沙区","广州珠江电力有限公司","1#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉检修","二氧化硫(mg/m3)","/",50,"/","/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/","/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/","/"]
[null,null,"2#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","停炉检修","二氧化硫(mg/m3)","/",50,"/","/"]
[{"$nulls":5},"氮氧化物(mg/m3)","/",100,"/","/"]
[{"$nulls":5},"汞(mg/m3)","/",0.03,"/","/"]
[null,null,"1#、2#锅炉烟囱排放口",null,null,"林格曼黑度（级）","/",1,"/","/"]
[null,null,"3#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019/1/10  汞由测试中心分析","二氧化硫(mg/m3)",23,50,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物(mg/m3)",39,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"3#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
[null,null,"4#锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019/1/11  汞由测试中心分析","二氧化硫(mg/m3)",25,50,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物(mg/m3)",35,100,"是"]
[{"$nulls":5},"汞(mg/m3)","ND(0.0025)",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"4#锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
["黄埔区","广州恒运热电（D）厂有限责任公司","9#（30万千瓦）锅炉\n处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-10","二氧化硫（mg/m3）",12,50,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物（mg/m3）",36,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"8#（30万千瓦）锅炉\n处理后",null,"2019-01-11","二氧化硫（mg/m3）",12,50,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物（mg/m3）",46,100,"是"]
[{"$nulls":5},"汞及其化合物（mg/m3）","ND(0.0025)",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"8#、9#(30万千瓦)锅炉烟囱排放口",null,"2019-01-10","林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
["黄埔区","鞍钢联众（广州）不锈钢有限公司","WRAP退火冷却段c","\n《轧钢工业大气污染物排放标准》（GB28665-2012）表2+广东省《大气污染物排放限值》（DB4427-2001）第二时段二级标准","2019-01-09","颗粒物（粉尘）（mg/m3）","<20",20,"是","广州市环境监测中心站"]
[null,null,"WRAP退火冷却段d",null,null,"颗粒物（粉尘）（mg/m3）","<20",20,"是"]
[null,null,"WRAP退火加热段a",null,null,"*颗粒物（烟尘）（mg/m3）","<20",20,"是"]
[null,null,"WRAP退火加热段b",null,null,"*颗粒物（烟尘）（mg/m3）","<20",20,"是"]
[null,null,"HAPL-ARP",null,"2019-01-10","氮氧化物（mg/m3）",16,120,"是"]
[{"$nulls":5},"氟化物（mg/m3）",0.33,9,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"CAPL中性电解区",null,"2019-01-10","硫酸雾（mg/m3）","ND(0.2)",10,"是"]
["花都区","广州市珠江水泥有限公司","窑尾","《水泥工业大气污染物排放标准》(GB 4519-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值\n","2019-01-11","*颗粒物（烟尘）(mg/m3)","<20",30,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物(mg/m3)",252,400,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)",22,100,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.05,"是"]
[{"$nulls":5},"氟化物(mg/m3)","ND（0.06）",3,"是"]
[{"$nulls":5},"氨(mg/m3)",0.3,10,"是"]
[null,null,"窑尾烟囱排放口",null,null,"林格曼黑度（级）",0.5,"/","是"]
[null,null,"下风向边界点1#",null,null,"总悬浮颗粒物(mg/m3)","0.104",0.5,"是"]
[null,null,"下风向边界点2#",null,null,"总悬浮颗粒物(mg/m3)","0.102",0.5,"是"]
[null,null,"上风向厂界外20米处",null,null,"总悬浮颗粒物(mg/m3)","0.100",0.5,"是"]
["花都区","广州市越堡水泥有限公司","回转窑尾","《水泥工业大气污染物排放标准》(GB 4915-2013)表1 现有与新建企业大气污染物排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表2规定的大气污染物最高允许排放限值+《水泥窑协同处置固体废物污染控制标准》表1协同处置固体废物水泥窑大气污染物最高允许排放浓度\n","2019-01-10","*颗粒物（烟尘）(mg/m3)","<20",30,"是","广州市环境监测中心站"]
[{"$nulls":5},"氮氧化物（mg/m3）",256,400,"是"]
[{"$nulls":5},"二氧化硫（mg/m3）",15,100,"是"]
[{"$nulls":4},"2019-01-10","汞（mg/m3）","ND(0.0025)",0.05,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[{"$nulls":5},"氟化氢（mg/m3）","ND(0.03)",1,"是"]
[{"$nulls":5},"氟化物（mg/m3）","ND(0.06)",3,"是"]
[{"$nulls":5},"氨（mg/m3）",12.43,10,"否"]
[null,null,"回转窑尾烟囱排放口",null,"2019-01-10","林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
[null,null,"上风向厂界外20米处","《水泥工业大气污染物排放标准》(GB 4915-2013)表3 大气污染物无组织排放限值+广东省《水泥工业大气污染物排放标准》(DB44 818-2010)表3作业场所颗粒物无组织排放限值","2019-01-09","总悬浮颗粒物（mg/m3）","0.099",0.5,"是","广州市环境监测中心站"]
[null,null,"下风向边界点1#",null,null,"总悬浮颗粒物（mg/m3）","0.105",0.5,"是"]
[{"$nulls":5},"氨（mg/m3）","0.10",{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"硫化氢（mg/m3）","ND（0.0003）",0.06,"是"]
[{"$nulls":5},"甲硫醚（mg/m3）","ND（0.0004）",0.07,"是"]
[{"$nulls":5},"甲硫醇（mg/m3）","ND（0.0006）",0.007,"是"]
[{"$nulls":5},"苯乙烯（mg/m3）","0.002",{"v":5,"d":"5.0"},"是"]
[{"$nulls":5},"二甲二硫（mg/m3）","ND（0.0004）",0.06,"是"]
[null,null,"下风向边界点2#",null,null,"总悬浮颗粒物（mg/m3）","0.108",0.5,"是"]
[{"$nulls":5},"氨（mg/m3）",0.12,{"v":1,"d":"1.0"},"是"]
[{"$nulls":5},"硫化氢（mg/m3）","ND（0.0003）",0.06,"是"]
[{"$nulls":5},"甲硫醚（mg/m3）","ND（0.0004）",0.07,"是"]
[{"$nulls":5},"甲硫醇（mg/m3）","ND（0.0006）",0.007,"是"]
[{"$nulls":5},"苯乙烯（mg/m3）","0.003",{"v":5,"d":"5.0"},"是"]
[{"$nulls":5},"二甲二硫（mg/m3）","ND（0.0004）",0.06,"是"]
[null,null,"厂界点1#",null,"2019-01-09","臭气浓度（无量纲）","<10",20,"是"]
[null,null,"厂界点2#",null,null,"臭气浓度（无量纲）","<10",20,"是"]
["黄埔区","广州恒运东区热力有限公司","5#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-14","氮氧化物（mg/m3）",34,100,"是","广州市环境监测中心站"]
[{"$nulls":5},"二氧化硫（mg/m3）","ND（3）",50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"5#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
[null,null,"4#75t/h锅炉处理后","《火电厂大气污染物排放标准》（GB13223-2011）表2大气污染物特别排放限值（燃煤锅炉）","2019-01-11","氮氧化物（mg/m3）",19,100,"是","广州市环境监测中心站"]
[{"$nulls":5},"二氧化硫（mg/m3）","ND（3）",50,"是"]
[{"$nulls":5},"汞及其化合物(mg/m3)","ND（0.0025）",0.03,"是","广东省测试分析研究所（中国广州分析测试中心）"]
[null,null,"4#75t/h锅炉烟囱排放口",null,null,"林格曼黑度（级）",0.5,1,"是","广州市环境监测中心站"]
["南沙区","广州珠江天然气发电有限公司","1#发电机组","《火电厂大气污染物排放标准》（GB13223-2011）表1火力发电锅炉及燃气轮组大气污染物排放浓度限值（天然气锅炉及燃气轮组）","2019-01-14","氮氧化物(mg/m3)",28,50,"是","广州市环境监测中心站"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND（3）",35,"是"]
[null,null,"1#发电机组烟囱排放口",null,null,"林格曼黑度（级）",0,1,"是"]
[null,null,"2#发电机组烟囱排放口",null,null,"林格曼黑度（级）",0,1,"是"]
[null,null,"2#发电机组",null,null,"氮氧化物(mg/m3)",19,50,"是"]
[{"$nulls":5},"二氧化硫(mg/m3)","ND（3）",35,"是"]
["南沙区","广州越威纸业有限公司","停产"]
["荔湾区","广州发电厂有限公司","停产"]
["增城区","广州市旺隆热电有限公司","停产"]
["备注：","①结果中“ND”表示未检出，括号中数值为该项目检出限。"]
[null,"②表中*颗粒物（烟尘）均为实测浓度，按照GB/T 16157-1996修改单，采用本标准测定颗粒物浓度小于等于20 mg/m3时，测定结果表述为＜20 mg/m3,无法换算为基准含氧量状态下的基准排放浓度，故不做达标评价。"]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0,"flags":["formulas_cached_only"]}